## Hareri
BILL No: 1
Project : | BORESHA NABAD
County: | Mandera
Sub County: | Arabia
Location: | Hareri - GPS (Lat: 3.952697, Long:41.474215)
Description: | Solar System and Water Irrigation System Installation
| Item Description | Unit | Qty | Unit Price (Kshs) | Amount (Kshs)
A | Solarization Works & Submersible Pump
Element No.1:Supply and deliver to site, install and commission test the following:
1.1 | Supply and install submersible pump end with capacity to pump75m3/hour at a head of 10 meters with 5.5KW 3PH Pump c/w Sub-mortar. The contractor to specify the pump and include data sheet i.e. specification including performance curves | Set | 1
1.2 | Dayliff SV3 5.5KW 3PH Sunverter | Set | 1
1.3 | Dayliff 4"x3 Adaptor Set | No. | 1
1.4 | Adaptor Box 4x4x3mm | No. | 1
1.5 | Monocrystalline photo voltaic solar modules 665W, 24Vdc | No. | 12
1.6 | Dayliff 4ST 1000 DC/40A PV Disconnect Switch | No. | 1
1.7 | Earth rod complete with clamp | No. | 1
1.8 | Lightning Arrestor | No. | 1
1.9 | Copper Earth Cable 10mm2 | M | 50
1.1 | 8mm2 4 core underground cable (armoured) | M | 50
1.11 | 8mm2 - 4 core standard PVC flat submersible drop cable | M | 50
1.12 | Londex standard dual core cable (probe sensor) | M | 60
1.13 | Twin flat 8mm cable with earth (Wiring connection) | M | 60
1.14 | Well probe sensor | No. | 1
1.15 | GS sunverter steel fabricates enclosure 1000x500x350mm | No. | 1
1.16 | Design as per radiations day angle, fabrication and installation of solar support structure for the specified solar panels. Rate to include for system testing. Use 75mmx 75mmx3mm SHS vertical support, 75mmx75mmx3mm struts and 50mmx50mmx2mm SHS purlins sections to hold panels tight into position. All joints braced. Height of the structure 4m above ground. The structure design must be preapproved before installation by the clients engineers | LS | 1
1.17 | Installation Sundries (cable ties, insulation tape, spacing tape, splicing kit) etc) | Item | 1
1.18 | Solar security light (50W LED light, 120W Solar Module, 150Ah Sealed maintenance free battery, Dawn-to dusk controller, 6m high pole c/w battery box |  | 2
1.19 | Design and fabricate a floating platoon to house submersible pump in a horizontal pumping position including pump sleeve and 100m long 10mm wire rope and other accessories to facilitate fastening along the river bank | Lumpsum | 1
Sub Total
Element No.2 : Installation and Transportation
2.1 | Installation labour, testing and transportation to site | LS | 1
Sub Total
Total
B | Water Irrigation System Installation
1 | Element No.1: Excavations
1.1 | Excavation of pipe trench 300mm wide x 500mm deep in soft soil and backfill | M3 | 228.75
Sub Total
Element No.2: Pipe Works
2.1 | Supply, deliver to site, joint and lay the following PN10 HDPE pipes and Appurtenances, end pieces should be supplied with a plain take off. The opposite side matching should be supplied with a plain take off. Jointing by butt fusion on HDPE pipes to attain parent material strength at the joints. All fittings should be removable for ease of replacement or servicing. Tee-off points with gate valves should be supplied as per BoQ specifications
2.1 | PN10 110mm HDPE pipes as per the specification above | LM | 280
2.2 | PN10 90 mm HDPE pipes as per the specification above | LM | 1200
2.3 | PN10 63 mm HDPE pipes as per the specification above | LM | 100
2.4 | G.I pipe class B including cutting and threading both ends of 1000mm long pieces | LM | 35.2
Sub Total
3 | Element No.3: Pipe Fittings
Supply, deliver to site, joint and fix the following fittings
3.1 | 110mm HDPE Tee PN 10 | Pcs | 7
3.2 | 110mm HDPE Male adaptor | Pcs | 5
3.3 | 110mmx90mm HDPE reducing coupling (socket) | Pcs | 5
3.4 | 90mm HDPE Elbow | Pcs | 20
3.5 | 90mm HDPE ball cork | Pcs | 5
3.6 | 90mm HDPE Tee PN 10 | Pcs | 32
3.7 | 90mmx63mm reducing coupling | Pcs | 32
3.8 | 63mm HDPE Male adaptor | Pcs | 32
3.9 | 4" Non-return Valve (peggler) | Pcs | 1
3.1 | 2" G.I Elbow | Pcs | 64
3.11 | 2" G.I socket | Pcs | 32
3.12 | 2" HDPE threaded (Female) ball cork (valve) | pcs | 32
3.13 | 2" G.I Hexagonal nipple | Pcs | 64
3.14 | 2"x1" reducing bush | Pcs | 32
3.14 | 1" G.I long screw nipple | Pcs | 32
3.15 | PTFE Tape (pack of 10) | Packet | 10
Sub Total
Element No.4: Concrete Works
4.1 | Double layer thick concrete class 25 (1:2:4) plinth(500mm wide x500mm longx150mm thick) at the base and 150mm below the grounf level for all 30 G.I water outlet provisions. | m3 | 2.4
Sub Total
Total
| SUMMARY |  |  |  | AMOUNT
A | SOLARIZATION & PUMP INSTALLATION
B | WATER IRRIGATION SYSTEM INSTALLATION
GRAND TOTAL

## Neboi
BILL No: 2
Project : | BORESHA NABAD
County: | Mandera
Sub County: | Mandera East
Location: | Neboi - GPS (Lat: 3.951783, Long:41.79744)
Description: | Solar System and Water Irrigation System Installation
| Item Description | Unit | Qty | Unit Price (Kshs) | Amount (Kshs)
A | Solarization Works & Submersible Pump
Element No.1:Supply and deliver to site, install and commission test the following:
1.1 | Supply and install submersible pump end with capacity to pump75m3/hour at a head of 10 meters with 5.5KW 3PH Pump c/w Sub-mortar. The contractor to specify the pump and include data sheet i.e. specification including performance curves | Set | 1
1.2 | Dayliff SV3 5.5KW 3PH Sunverter | Set | 1
1.3 | Dayliff 4"x3 Adaptor Set | No. | 1
1.4 | Adaptor Box 4x4x3mm | No. | 1
1.5 | Monocrystalline photo voltaic solar modules 665W, 24Vdc | No. | 12
1.6 | ` | No. | 1
1.7 | Earth rod complete with clamp | No. | 1
1.8 | Lightning Arrestor | No. | 1
1.9 | Copper Earth Cable 10mm2 | M | 50
1.1 | 8mm2 4 core underground cable (armoured) | M | 50
1.11 | 8mm2 - 4 core standard PVC flat submersible drop cable | M | 50
1.12 | Londex standard dual core cable (probe sensor) | M | 60
1.13 | Twin flat 8mm cable with earth (Wiring connection) | M | 60
1.14 | Well probe sensor | No. | 1
1.15 | GS sunverter steel fabricates enclosure 1000x500x350mm | No. | 1
1.16 | Design as per radiations day angle, fabrication and installation of solar support structure for the specified solar panels. Rate to include for system testing. Use 75mmx 75mmx3mm SHS vertical support, 75mmx75mmx3mm struts and 50mmx50mmx2mm SHS purlins sections to hold panels tight into position. All joints braced. Height of the structure 4m above ground. The structure design must be preapproved before installation by the clients engineers | LS | 1
1.17 | Installation Sundries (cable ties, insulation tape, spacing tape, splicing kit) etc) | Item | 1
1.18 | Solar security light (50W LED light, 120W Solar Module, 150Ah Sealed maintenance free battery, Dawn-to dusk controller, 6m high pole c/w battery box |  | 2
1.19 | Design and fabricate a floating platoon to house submersible pump in a horizontal pumping position including pump sleeve and 100m long 10mm wire rope and other accessories to facilitate fastening along the river bank | Lumpsum | 1
Sub Total
Element No.2 : Installation and Transportation
2.1 | Installation labour, testing and transportation to site | LS | 1
Sub Total
Total
B | Water Irrigation System Installation
1 | Element No.1: Excavations
1.1 | Excavation of pipe trench 300mm wide x 500mm deep in soft soil and backfill | M3 | 228.75
Sub Total
Element No.2: Pipe Works
2.1 | Supply, deliver to site, joint and lay the following PN10 HDPE pipes and Appurtenances, end pieces should be supplied with a plain take off. The opposite side matching should be supplied with a plain take off. Jointing by butt fusion on HDPE pipes to attain parent material strength at the joints. All fittings should be removable for ease of replacement or servicing. Tee-off points with gate valves should be supplied as per BoQ specifications
2.1 | PN10 110mm HDPE pipes as per the specification above | LM | 280
2.2 | PN10 90 mm HDPE pipes as per the specification above | LM | 1200
2.3 | PN10 63 mm HDPE pipes as per the specification above | LM | 100
2.4 | G.I pipe class B including cutting and threading both ends of 1000mm long pieces | LM | 35.2
Sub Total
3 | Element No.3: Pipe Fittings
Supply, deliver to site, joint and fix the following fittings
3.1 | 110mm HDPE Tee PN 10 | Pcs | 7
3.2 | 110mm HDPE Male adaptor | Pcs | 5
3.3 | 110mmx90mm HDPE reducing coupling (socket) | Pcs | 5
3.4 | 90mm HDPE Elbow | Pcs | 20
3.5 | 90mm HDPE ball cork | Pcs | 5
3.6 | 90mm HDPE Tee PN 10 | Pcs | 32
3.7 | 90mmx63mm reducing coupling | Pcs | 32
3.8 | 63mm HDPE Male adaptor | Pcs | 32
3.9 | 4" Non-return Valve (peggler) | Pcs | 1
3.1 | 2" G.I Elbow | Pcs | 64
3.11 | 2" G.I socket | Pcs | 32
3.12 | 2" HDPE threaded (Female) ball cork (valve) | pcs | 32
3.13 | 2" G.I Hexagonal nipple | Pcs | 64
3.14 | 2"x1" reducing bush | Pcs | 32
3.14 | 1" G.I long screw nipple | Pcs | 32
3.15 | PTFE Tape (pack of 10) | Packet | 10
Sub Total
Element No.4: Concrete Works
4.1 | Double layer thick concrete class 25 (1:2:4) plinth(500mm wide x500mm longx150mm thick) at the base and 150mm below the grounf level for all 30 G.I water outlet provisions. | m3 | 2.4
Sub Total
Total
| SUMMARY |  |  |  | AMOUNT
A | SOLARIZATION & PUMP INSTALLATION
B | WATER IRRIGATION SYSTEM INSTALLATION
GRAND TOTAL

## Summary Sheet
SUMMARY SHEET
No | Bill No | Estimated Amount
1 | Bill No. 1: Solar + Irri - Site 1 | 0
2 | Bill No. 1: Solar + Irri - Site 2 | 0
| Grand Total | 0