## Budget Summary
SUMMARY SHEET
No | Bill No | Estimated Amount
1 | Bill No. 1: Malkapunda Shallow Well
2 | Bill No. 2 : Fikow Shallow Well
3 | Bill No. 3: Koromey Shallow Well
4 | Bill No. 4 : Haji Kerow Shallow Well
5 | Bill No. 5 : Malkakuna Shallow Well
6 | Bill No. 6 : Girisa Shallow Well
Grand Total

## Malkapunda Shallow Well
BILL No: 1
Project : | BORESHA
County: | Mandera
Sub County: | Mandera East
Site Location: | Malkapunda Shallow Well
Description: | Shallow Well Solarization, & Pipeline Extension (100M)
Item No | Item Description | Unit | Qty | Rate | Amount
A | Borehole Solarization
Element No.1: Supply and deliver to site, install, commission and test the following for pumping 6m3/hr with 7.5 Kw Motor size
1.1 | Supply and install a Submersible pump end, capable of pumping 10m3/hr against a head of 15m, complete with borehole cables. The Pump should be complete with a 1.1KW single phase motor. The contractor to specify the Pump and include data sheet i.e. specification including performance curves | Set | 1
1.2 | 2" Dayliff medium duty pipes and sockets | No. | 3
1.3 | Dayliff 2" Adaptor Set | No. | 1
1.4 | Adaptor Box 4x4x3mm | No. | 1
1.5 | Dayliff SV3 2KW single phase Sunverter | Set | 1
1.6 | Monocrystalline photo voltaic solar modules 320W, 24Vdc | No. | 6
1.7 | Dayliff 4ST 1000 DC/40A PV Disconnect Switch | No. | 1
1.8 | Earth rod complete with clamp | No. | 1
1.9 | Lightning Arrestor | No. | 1
1.1 | Copper Earth Cable 4mm2 | M | 25
1.11 | 4mm2 4 core underground cable (armoured) | M | 25
1.12 | 1.5mm2- 2 core underground armoured cable(elecrode sensor) | M | 25
1.13 | Twin flat10mm cable with earth (Wiring connection) | M | 35
1.14 | GS sunverter steel fabricated rectangular enclosure 600mm in length x500 in width x350mm in breath to be mounted on the 75mmx75mm x3mm SHS vertical support solar structure vertical support. | No. | 1
1.15 | Design as per daily radiations angle, fabricate and installation of solar support structure for the specified solar panels. Rate to include for system testing. Use 50mmx 50mmx3mm SHS vertical support, 32mmx32mmx3mm struts and 25mmx25mmx2mm SHS purlins sections to hold panels tight into position. All joints braced. Height of the structure 2.8m above ground on the higher elevation. The structure design must be preapproved before installation by the clients engineers. | LS | 1
1.16 | Installation Sundries (cable ties, insulation tape, spacing tape, spicing joints etc) | Item | 1
1.17 | Solar security light (50W LED light, 120W Solar Module, 150Ah Sealed maintenance free battery, Dawn-to dusk controller, 6m high pole c/w battery box |  | 1
Sub Total
Element No.2 : Installation and Transportation
2.1 | Installation labour, testing and transportation to site | LS | 1
Sub Total
Total
B) | Construction of 500mm High Shallow Well Protection Wall and Shallow Well Cover
Element No. 1 : Concrete Walling
1.1 | Cast 200mm reinforced concrete vertical wall reinforced with 10mm twisted bars spaced@200mm c/c concrete mix ratio 1:2:4. | m3 | 0.5024
1.2 | Cast 200mm reinforced concrete slab reinforced with10mm twisted bars spaced@200mm c/c concrete mix ratio 1:2:4. | m3 | 0.30144
Sub Total
Element No. 2: Concrete Ancillaries
2.1 | Formwork
Provide cut and fix in position sawn timber (150mmx25mm) formwork or equivalent.
2.1.1 | Sides of the vertical concrete wall and shallow well cover slab | m2 | 7.7872
2.1.2 | 5m long support props for supporting the formwork | Pcs | 5
2.2 | Reinforcement
Steel reinforcement cut, bend & placed in position, unit price to include cutting, bending & placing in position with binding wire and concrete seats
2.2.2 | Provide and place 10mm diameter high tensile steel (0.67kg/m on the the walls | KG | 35.577
Sub Total
Element No.3: Other Fixtures
3.1 | Construct 800mmx 800mm lockable inspection steel cover on the top slab | No. | 1
Sub Total
Element No. 4 : Finishing Works
4.1 | 20mm thick 1:3 cement /sand mortar plaster mixed with water proof cement to external walls and cover slab. | SM | 5.2752
Sub Total
Total
C | Pipeline Extension
Element No. 1 : Plumbing and Piping Works
1.1 | Excavation
1.1.1 | Excavation of pipe trench 300mm wide x600mm deep in soft soil and backfill for a pipeline trench 100 meters long | m3 | 18
2.2 | Pipe works
Supply, deliver to site, joint and lay the following PN10 HDPE pipes. Jointing by butt fusion on HDPE pipes to attain parent material strength at the joints. All fittings should be removable for ease of replacement or servicing. Tee-off points with gate valves should be supplied as per pipeline.
2.2.1 | PN10 90mm HDPE pipes as per the specification above | LM | 100
2.3 | Pipe Fittings
Supply, deliver to site, joint and fix the following fittings
2.3.1 | 90mmx63mm HDPE male adaptor | Pcs | 2
2.3.2 | 2" Dia G.I sockets | Pcs | 6
2.3.3 | 2" Dia G.I Elbows | Pcs | 6
2.3.4 | 2" Dia ball cock (peggler) | Pcs | 1
2.3.5 | 2" Dia G.I Pipe Class B | No. | 1
2.3.6 | 2" Dia Non-return valve | No. | 1
2.3.7 | 2" Dia G.I union | No. | 2
2.3.8 | 2" Dia Hexahonal Nipple | No. | 4
2.3.9 | 2" Dayliff medium duty pipes and sockets | No. | 3
2.3.10 | PTFE Tape (Packet of 10 rolls) | Packet | 2
Sub Total
Total
| SUMMARY |  |  |  | AMOUNT
A | BOREHOLE SOLARIZATION
B | CONSTRUCTION OF 500MM HIGH SHALLOW WELL LINING & WELL COVER
C | PIPELINE EXTENSION
GRAND TOTAL

## Fikow Shallow Well
BILL No: 2
Project : | BORESHA
County: | Mandera
Sub County: | Mandera East
Site Location: | Fikow Shallow Well
Description: | Construction of 1500m High Shallow Well Potection Wall
Item No | Item Description | Unit | Qty | Rate | Amount
A | Construction of 1500m High Shallowe Well Potection Wall
Element No.1: Hacking
1.1 | Hack shalllow well floor slab, 200mm from the edge. | Lumpsum | 1
Sub Total
Element No. 2 : Concrete Walling
2.1 | Cast 200mm reinforced concrete vertical wall from shallow well cover slab reinforced with 10mm twisted bars spaced@200mm c/c concrete mix ratio 1:2:4. | m3 | 2.6376
Sub Total
Element No. 3: Concrete Ancillaries
3.1 | Formwork
Provide cut and fix in position sawn timber (150mmx25mm) formwork or equivalent.
3.1.1 | Sides of the vertical concrete wall | m2 | 26.376
3.1.2 | 5m long support props for supporting the formwork | Pcs | 5
3.2 | Reinforcement
Steel reinforcement cut, bend & placed in position, unit price to include cutting, bending & placing in position with binding wire and concrete seats
3.2.2 | Provide and place 10mm diameter high tensile steel (0.67kg/m on the the walls | KG | 93.465
Sub Total
Element No. 4 : Finishing Works
4.1 | 20mm thick 1:3 cement /sand mortar plaster to both internal and extenal walls | SM | 28.776
Sub Total
Grant Total
| SUMMARY |  |  |  | AMOUNT
A | CONSTRUCTION OF SHALLOW WELL PROTECTION WALL
GRAND TOTAL

## Koromey Shallow Well
BILL No: 3
Project : | BORESHA
County: | Mandera
Sub County: | Mandera East
Site Location: | Koromey
Description: | Borehole Solarization and Extension of Shallow Well Lining and Cover Slab
Item No | Item Description | Unit | Qty | Rate | Amount
A | Borehole Solarization
Element No.1: Supply and deliver to site, install, commission and test the following for pumping 6m3/hr
| Supply and install a Submersible pump end, capable of pumping 5m3/hr against a head of 15m, complete with borehole cables. The Pump should be complete with a 1.1KW single phase motor. The contractor to specify the Pump and include data sheet i.e. specification including performance curves | Set | 1
1.1 | Dayliff SV3 2KW single phase Sunverter | Set | 1
1.2 | Monocrystalline photo voltaic solar modules 320W, 24Vdc | No. | 6
1.3 | Dayliff 4ST 1000 DC/40A PV Disconnect Switch | No. | 1
1.4 | Earth rod complete with clamp | No. | 1
1.5 | Lightning Arrestor | No. | 1
1.6 | Copper Earth Cable 4mm2 | M | 25
1.7 | 4mm2 4 core underground cable (armoured) | M | 25
1.8 | 1.5mm2- 2 core underground armoured cable(elecrode sensor) | M | 25
1.9 | Twin flat10mm cable with earth (Wiring connection) | M | 35
1.1 | GS sunverter steel fabricated rectangular enclosure 600mm in length x500 in width x350mm in breath to be mounted on the 75mmx75mm x3mm SHS vertical support solar structure vertical support. | No. | 1
1.11 | Design as per daily radiations angle, fabricate and installation of solar support structure for the specified solar panels. Rate to include for system testing. Use 50mmx 50mmx3mm SHS vertical support, 32mmx32mmx3mm struts and 25mmx25mmx2mm SHS purlins sections to hold panels tight into position. All joints braced. Height of the structure 2.8m above ground on the higher elevation. The structure design must be preapproved before installation by the clients engineers. | LS | 1
1.12 | Installation Sundries (cable ties, insulation tape, spacing tape, spicing joints etc) | Item | 1
Sub Total
Element No.2 : Installation and Transportation
2.1 | Installation labour, testing and transportation to site | LS | 1
Sub Total
Total
B | Construction of 1500mm High Shallow Well Wall Extension and Well Cover Slab
Element No. 1 : Concrete Walling
1.1 | Cast 200mm reinforced concrete vertical wall reinforced with 10mm twisted bars spaced@200mm c/c concrete mix ratio 1:2:4. | m3 | 2.2608
1.2 | Cast 200mm reinforced concrete slab reinforced with10mm twisted bars spaced@200mm c/c concrete mix ratio 1:2:4. | m3 | 0.67824
Sub Total
Element No. 2: Concrete Ancillaries
2.1 | Formwork
Provide cut and fix in position sawn timber (150mmx25mm) formwork or equivalent.
2.1.1 | Sides of the vertical concrete wall and shallow well cover slab | m2 | 28.26
2.1.2 | 5m long support props for supporting the formwork | Pcs | 10
2.2 | Reinforcement
Steel reinforcement cut, bend & placed in position, unit price to include cutting, bending & placing in position with binding wire and concrete seats
2.2.2 | Provide and place 10mm diameter high tensile steel (0.67kg/m on the the walls | KG | 115.24
Sub Total
Element No.3: Other Fixtures
3.1 | Construct 800mmx 800mm lockable inspection steel cover on the top slab | No. | 1
Sub Total
Element No. 4 : Finishing Works
4.1 | 20mm thick 1:3 cement /sand mortar plaster mixed with water proof cement to external walls and cover slab. | SM | 16.956
Sub Total
Total
| SUMMARY |  |  |  | AMOUNT
A | BOREHOLE SOLARIZATION
B | CONSTRUCTION OF SHALLOW WELL PROTECTION WALL
GRAND TOTAL

## Haji Kerow
BILL No: 4
Project : | BORESHA
County: | Mandera
Sub County: | Mandera East
Site Location: | Haji Kerow
Description: | Borehole Solarization, Farm Irrigation Installation and Well Lining Extension
Item No | Item Description | Unit | Qty | Rate | Amount
A | Borehole Solarization
Element No.1: Supply and deliver to site, install, commission and test the following for pumping 6m3/hr
1.1 | Supply and install a submersible pump end, capable of pumping 10m3/hr against a head of 15m, complete with borehole cables. The Pump should be complete with a 1.1KW single phase motor. The contractor to specify the Pump and include data sheet i.e. specification including performance curves | Set | 1
1.2 | 2" Dayliff medium duty pipes and sockets | No. | 3
1.3 | Dayliff 2" Adaptor Set | No. | 1
1.4 | Adaptor Box 4x4x3mm | No. | 1
1.5 | Dayliff SV3 2KW single phase Sunverter | Set | 1
1.6 | Monocrystalline photo voltaic solar modules 320W, 24Vdc | No. | 6
1.7 | Dayliff 4ST 1000 DC/40A PV Disconnect Switch | No. | 1
1.8 | Earth rod complete with clamp | No. | 1
1.9 | Lightning Arrestor | No. | 1
1.1 | Copper Earth Cable 4mm2 | M | 25
1.11 | 4mm2 4 core underground cable (armoured) | M | 25
1.12 | 1.5mm2- 2 core underground armoured cable(elecrode sensor) | M | 25
1.13 | Twin flat10mm cable with earth (Wiring connection) | M | 35
1.14 | GS sunverter steel fabricated rectangular enclosure 600mm in length x500 in width x350mm in breath to be mounted on the 75mmx75mm x3mm SHS vertical support solar structure vertical support. | No. | 1
1.15 | Design as per daily radiations angle, fabricate and installation of solar support structure for the specified solar panels. Rate to include for system testing. Use 50mmx 50mmx3mm SHS vertical support, 32mmx32mmx3mm struts and 25mmx25mmx2mm SHS purlins sections to hold panels tight into position. All joints braced. Height of the structure 2.8m above ground on the higher elevation. The structure design must be preapproved before installation by the clients engineers. | LS | 1
1.16 | Installation Sundries (cable ties, insulation tape, spacing tape, spicing joints etc) | Item | 1
1.17 | Solar security light (50W LED light, 120W Solar Module, 150Ah Sealed maintenance free battery, Dawn-to dusk controller, 6m high pole c/w battery box |  | 1
Sub Total
Element No.2 : Installation and Transportation
2.1 | Installation labour, testing and transportation to site | LS | 1
Sub Total
Total
B | Water Irrigation System Installation
1 | Element No.1: Excavations
1.1 | Excavation of pipe trench 300mm wide x 500mm deep in soft soil and backfill | M3 | 72.45
Sub Total
Element No.2: Pipe Works
2.1 | Supply, deliver to site, joint and lay the following PN10 HDPE pipes and Appurtenances, end pieces should be supplied with a plain take off. The opposite side matching should be supplied with a plain take off. Jointing by butt fusion on HDPE pipes to attain parent material strength at the joints. All fittings should be removable for ease of replacement or servicing. Tee-off points with gate valves should be supplied as per BoQ specifications
2.2 | PN10 90 mm HDPE pipes as per the specification above | LM | 765
2.3 | PN10 63 mm HDPE pipes as per the specification above | LM | 100
2.4 | G.I pipe class B including cutting and threading both ends of 1000mm long pieces | LM | 13.2
Sub Total
3 | Element No.3: Pipe Fittings
Supply, deliver to site, joint and fix the following fittings
3.1 | 90mm HDPE Tee PN 10 | Pcs | 5
3.2 | 90mm x63mm HDPE male adaptor | Pcs | 2
3.3 | 90mm x75mm HDPE male adaptor | Pcs | 2
3.3 | 90mm HDPE Elbow | Pcs | 16
3.4 | 90mm HDPE ball cork | Pcs | 4
3.5 | 90mm HDPE Tee PN 10 | Pcs | 14
3.6 | 90mmx63mm reducing coupling | Pcs | 14
3.7 | 63mm HDPE Male adaptor | Pcs | 14
3.8 | 2" G.I socket | Pcs | 3
3.9 | 2" G.I elbow | Pcs | 6
3.1 | 2" G.I union | Pcs | 2
3.11 | 2" G.I Elbow | Pcs | 28
3.12 | 2" G.I socket | Pcs | 14
3.13 | 2" HDPE threaded (Female) ball cork (valve) | pcs | 14
3.14 | 2" G.I Hexagonal nipple | Pcs | 28
3.16 | 2"x1" reducing bush | Pcs | 14
3.17 | 1" G.I long screw nipple | Pcs | 14
3.18 | PTFE Tape (pack of 10) | Packet | 8
Sub Total
Element No.4: Concrete Works
4.1 | Double layer thick concrete class 25 (1:2:4) plinth(500mm wide x500mm longx150mm thick) at the base and 150mm below the grounf level for all 30 G.I water outlet provisions. | m3 | 1.05
Sub Total
Total
C) | Construction of 500mm High Shallow Well Protection Wall and Shallow Well Cover
Element No. 1 : Concrete Walling
1.1 | Cast 200mm reinforced concrete vertical wall reinforced with 10mm twisted bars spaced@200mm c/c concrete mix ratio 1:2:4. | m3 | 0.5652
1.2 | Cast 200mm reinforced concrete slab reinforced with10mm twisted bars spaced@200mm c/c concrete mix ratio 1:2:4. | m3 | 0.38151
Sub Total
Element No. 2: Concrete Ancillaries
2.1 | Formwork
Provide cut and fix in position sawn timber (150mmx25mm) formwork or equivalent.
2.1.1 | Sides of the vertical concrete wall and shallow well cover slab | m2 | 9.0432
2.1.2 | 5m long support props for supporting the formwork | Pcs | 7
2.2 | Reinforcement
Steel reinforcement cut, bend & placed in position, unit price to include cutting, bending & placing in position with binding wire and concrete seats
2.2.2 | Provide and place 10mm diameter high tensile steel (0.67kg/m on the the walls | KG | 43.55
Sub Total
Element No.3: Other Fixtures
3.1 | Construct 800mmx 800mm lockable inspection steel cover on the top slab | No. | 1
Sub Total
Element No. 4 : Finishing Works
4.1 | 20mm thick 1:3 cement /sand mortar plaster mixed with water proof cement to external walls and cover slab. | SM | 6.2172
4.2 | 20mm thick 1:3 cement /sand mortar plaster mixed with water proof cement to internal walls (4 meters from ground level) of the shallow wells | SM | 22.608
Sub Total
Total
| SUMMARY |  |  |  | AMOUNT
A | BOREHOLE SOLARIZATION
C | FARM IRRIGATION SYSTEM
D | CONSTRUCTION OF PROTECTION WALL AND COVER
GRAND TOTAL

## Malkakuna
BILL No: 5
Project : | BORESHA NABAD
County: | Mandera
Sub County: | Mandera North
Site Location: | Malkakuna
Description: | Construction of 500mm High Shallow Well Protection Wall and Shallow Well Cover
Item No | Item Description | Unit | Qty | Rate | Amount
A) | Construction of 500mm High Shallow Well Protection Wall and Shallow Well Cover
Element No. 1 : Concrete Walling
1.1 | Cast 200mm reinforced concrete vertical wall reinforced with 10mm twisted bars spaced@200mm c/c concrete mix ratio 1:2:4. | m3 | 0.4867
1.2 | Cast 200mm reinforced concrete slab reinforced with10mm twisted bars spaced@200mm c/c concrete mix ratio 1:2:4. | m3 | 0.28289
Sub Total
Element No. 2: Concrete Ancillaries
2.1 | Formwork
Provide cut and fix in position sawn timber (150mmx25mm) formwork or equivalent.
2.1.1 | Sides of the vertical concrete wall and shallow well cover slab | m2 | 7.483
2.1.2 | 5m long support props for supporting the formwork | Pcs | 5
2.2 | Reinforcement
Steel reinforcement cut, bend & placed in position, unit price to include cutting, bending & placing in position with binding wire and concrete seats
2.2.2 | Provide and place 10mm diameter high tensile steel (0.67kg/m on the the walls | KG | 34.907
Sub Total
Element No.3: Other Fixtures
3.1 | Construct 800mmx 800mm lockable inspection steel cover on the top slab | No. | 1
Sub Total
Element No. 4 : Finishing Works
4.1 | 20mm thick 1:3 cement /sand mortar plaster mixed with water proof cement to external walls and cover slab. | SM | 5.0495
Sub Total
Total
| SUMMARY |  |  |  | AMOUNT
A | CONSTRUCTION OF PROTECTION WALL AND COVER SLAB
GRAND TOTAL

## Girisa Shallow Well
BILL No: 6
Project : | BORESHA NABAD
County: | Mandera
Sub County: | Mandera North
Site Location: | Girisa Shallow Well
Description: | Construction of 1500mm High Shallow Well Protection Wall and Shallow Well Cover
Item No | Item Description | Unit | Qty | Rate | Amount
A) | Construction of 1500m High Shallow Well Protection Wall and Shallow Well Cover
Element No. 1 : Concrete Walling
1.1 | Cast 200mm reinforced concrete vertical wall reinforced with 10mm twisted bars spaced@200mm c/c concrete mix ratio 1:2:4. | m3 | 2.0724
1.2 | Cast 200mm reinforced concrete slab reinforced with10mm twisted bars spaced@200mm c/c concrete mix ratio 1:2:4. | m3 | 0.56991
Sub Total
Element No. 2: Concrete Ancillaries
2.1 | Formwork
Provide cut and fix in position sawn timber (150mmx25mm) formwork or equivalent.
2.1.1 | Sides of the vertical concrete wall and shallow well cover slab | m2 | 25.5596
2.1.2 | 5m long support props for supporting the formwork | Pcs | 5
2.2 | Reinforcement
Steel reinforcement cut, bend & placed in position, unit price to include cutting, bending & placing in position with binding wire and concrete seats
2.2.2 | Provide and place 10mm diameter high tensile steel (0.67kg/m on the the walls | KG | 99.227
Sub Total
Element No.3: Other Fixtures
3.1 | Construct 800mmx 800mm lockable inspection steel cover on the top slab | No. | 1
Sub Total
Element No. 4 : Finishing Works
4.1 | 20mm thick 1:3 cement /sand mortar plaster mixed with water proof cement to external walls and cover slab. | SM | 15.1976
Sub Total
Total
| SUMMARY |  |  |  | AMOUNT
A | CONSTRUCTION OD PRPTECTION WALL AND COVER
GRAND TOTAL