Annex F

West Area Office

Lot# 2.1.A to 2.4.A

ITB-AFG-AFC-010-2026 – Supply and Delivery of Water Supply System (Equipment and Materials)

List of required items for sample check bidders must fill out and complete this Annex F to provide proof of the availability of the following items, including locations and current stock levels.

Lot#2.1. A- Construction Materials

| S/N | Items | Specification | Location and Current Stock Levels | Remarks |
| --- | --- | --- | --- | --- |
| 1 | Stone | Stone should be Mountain not plain and sea stone, its mark should be 400, weight of stones. Should be 5- 40 kilograms and should has relatively regular dimensions that can make reasonable feces of stonemasonry, and more than 60 % has side view stone the special weight of the stones should not be low from 2.5 tons/m3 and in 24 hours under water more than 5 percent water does not absorb The size of the stones is between (25-50 cm) the stones are not contaminated with soil and mud |  |  |
| 2 | Sand | Washed sand (0.075-4.76 m) is not red from Sand and gravel Washed plant It shald be free from Soil, logs, stumps, roots and rubbish. The materials passing sieve 0.075mm should not be greater than 5%. |  |  |
| 3 | Cement | Cement with updated date and should be powder and the quality should be equal to Shraq Asia cement with bag 50 kg in weight. |  |  |
| 4 | Steel bar | Supply and Delivery of Steel Reinforcement Bars: Steel Reinforcement Bars Grades 60 which has yield strength of 60,000 psi with deferent sizes 8mm, 10mm, 16mm, 18mm The steel must pass the bend test requirements as prescribed in the referenced ASTM A615 standard. Test specimens shall withstand being bent around a pin (mandrel) without cracking on the outside radius. The diameter of the pin and the angle of the bend (typically 90° or 180) Similar to Kabul Folad. |  |  |

Lot# 2.2. A- Pipe and fittings

| S/N | Items | Specification | Location and Current Stock Levels | Remarks |
| --- | --- | --- | --- | --- |
| 1 | PVC Pipe | 3-inch PVC pipe is a versatile, lightweight, and durable rigid tubing widely used for residential plumbing, irrigation, and wire protection. It features a nominal outside diameter (OD) of roughly 3 to 3.5 inches (75 mm to88.9 mm depending on the standard. Core Specifications Nominal Size: 3 inches80 mm metric equivalent) Outer Diameter (OD): Typically 75 mm2.95 inches for standard or metric pipe, or 88.9 mm 3.5 inches for Schedule 40 Class E pressure pipes. Wall Thickness: Ranges from 3 mm to 5.5 mm, depending on whether the pipe is rated for light-duty or heavy-pressure applications. Pressure Ratings: Varies greatly. Non-pressure (Class O) pipes are for gravity flow, while Schedule 40 or Class E/7 pipes can handle working pressures from 6 kg/cm^2 up to17.9 bar\260 psi.Common ApplicationsPlumbing & Drainage: Primarily used for drain, and vent (DWV) lines, as well as main sewer lines. |  |  |
| 2 | GI Pipe | Pipe insulation GI. sheet 0.5 mm Covering (for supply, inflow and drainpipes) |  |  |
| 3 | PE Pipe | 90 mm (3 inch) PE 100 PN10 HDPE pipe with high-density polyethylene pipe, frequently used for water supply, offering 10 bar pressure resistance. Commonly manufactured to SDR 17 or 13.6, it has a wall thickness of approximately5.4 mm to 6.7 mm and is ideal for potable water, featuring corrosion resistance, flexibility, and longevity |  |  |
| 4 | Cast Iron Flanged Valve | "The 2" Cast Iron Flanged Globe Valve with Flange Adapter offers a safe and fully adjustable solution for regulating water, HVAC or water systems, typically rated at 125/150# and a rising or non-rising stem (NRS) for tight spaces. Often featuring bronze trim or flexible EPDM seats, these valves are resistant to pipeline stresses and allow for easy, weld-free, and serviceable connections to pipes using flange adapters. Size: 2" (DN50). Material: Cast iron body with bronze-mounted seats (IBBM) or flexible EPDM seats for a tight seal. Flange Standard: Typically, Class 125/150 or PN10/PN16. Stem Type: Non-rising stem (NRS) for underground/confined space, or external bolt and yoke (OS&Y) for easy position monitoring. Connection: Flanged ends; Flange adapters allow these valves to be connected to plain end piping systems." |  |  |
| 5 | Water Meter | 0.5-inch (15mm) plastic water meter is a compact, lightweight flow measurement device used for domestic or light industrial applications, typically measuring flow in GPM (Gallons Per Minute) or LPM (Liters Per Minute). Common 0.5-inch plastic, such as the Accuflow Water Meter, often use a multi-jet, dry-dial design for high accuracy and corrosion resistance. Key Specifications & Typical Features Size: 15mm (inch) nominal diameter. Material: Plastic body (ABS or Nylon), ensuring durability and corrosion resistance. Flow Range: Often covers ranges like GPM (LPM) or similar. |  |  |
| 6 | Tee | PE Equal Tee 90 mm, PN-16 |  |  |
| 7 | Coupling | PE Reducing Coupling 110 x 75 mm |  |  |

Lot#2.3. A- Solar system

| S/N | Items | Specification | Location and Current Stock Levels | Remarks |
| --- | --- | --- | --- | --- |
| 1 | Pedrolla pump | Submersible pump equal to Pedrolla and have this specification : Model : 4SR8/31 Power: 5.5 kw Hours power: 7.5HP Current: 12.3 A out let: 2inch Voltage: 380V Phase: 3 pahse Diameter: 4 inch |  |  |
| 2 | Electrical Cable | Electrical Cable 4×2.5 mm² for Water Pump: Flexible copper conductor cable with four cores, each having a cross-sectional area of 2.5 mm², insulated with PVC and suitable for powering and controlling water pumps. It provides reliable conductivity, mechanical strength, and resistance to moisture, heat, and outdoor operating conditions. |  |  |
| 3 | Solar Panels | Solar panels equal to Tommatech 545 Wp mono-crystalline solar panels have these key performance and compatibility implications: • It is a high-power (545 Wp) module with 21.03% efficiency and power tolerance of 0 to +5 W, so actual production should be at or slightly above the rated 545 W. • The panel’s operating (maximum power) point is: o Vmp = 42.2 V o Imp = 12.92 A • For safety in real-world conditions (especially cold weather), the open-circuit voltage is: o Voc = 50 V • The panels short-circuit current is: o Isc = 13.76 A • The panel is rated for: o Maximum system voltage: 1500 V DC (overall upper limit for system design) o Maximum series fuse rating: 25 A (choose fuses at/within this limit) Protection class: Class II (insulation/safety category) • Temperature range suitability: o Operating temperature: -40°C to +85°C. • For designing of system: Use Voc (50 V) to ensure your string voltage in the coldest conditions stays within your inverter/MPPT limit. Use Vmp (42.2 V), Imp (12.92 A), and Isc (13.76 A) for matching MPPT/charge-controller current and voltage operating ranges, and for selecting correct protection |  |  |
| 4 | Panel Board | Electrical Panel Board (Medium Size): Medium-size electrical panel board fabricated from durable metal enclosure, suitable for outdoor installation, with capacity to accommodate a minimum of five fuse units and related electrical components. The supplier shall provide all required internal wiring, connections, terminals, and assembly necessary to deliver a complete, ready-for-installation electrical panel. |  |  |

Lot#2.4. A- Drilling and testing

| S/N | Items | Specification | Location and Current Stock Levels | Remarks |
| --- | --- | --- | --- | --- |
| 1 | PVC Pipe 8 inch | Supply and installation of PVC casing pipe with diameter of 8'' Class D. |  |  |

Note: This Annex F must be signed by the Suppliers, confirming that the listed items are available at their respective location and indicating the offered quantity of each item they can provide.

Sign: _________________

Date: _________________

Stamp: ________________